|  |
| --- |
| **Tool/Equipment Details** |
|

|  |
| --- |
|  |
| Tool/Equipment Description |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  |  |  |  |  |
| Brand |  | Model / Identification No. |  | Sydney Trains Asset No. |

|  |  |  |
| --- | --- | --- |
|  |  |  |
| IR Tester Asset No.: |  | IR Tester Next Calibration Date: |

 |

|  |
| --- |
| **For guidance on how to complete this form, please refer to:** |
| * SP D 79041 Insulated Sticks, Tools and Equipment used for work near or on/within Exposed Electrical Equipment – Inspection, Testing, Care and Maintenance
* D2013/80872 Inspection and Testing of Insulated Sticks, Tools and Equipment used for work On or Near Exposed 1500V OHW or Equipment
 |

|  |
| --- |
| **The Insulated Stick, Tool or Equipment is used for work On or Near Exposed 1500V?** |
| Delete the appropriate words from the heading above.In documenting this determination refer to the work specific SWI and D2013/80872 section titled “Inspection and Test Philosophy”.Note: The IR tests to be performed are dictated by this determination. |

|  |
| --- |
| **Visual Inspection** |
| Check finish of insulated stick, tool, equipment and accessories has no cracks, surface damage, or mechanical defects, etc.A 3 month inspection period is only required for tools & equipment used “On” exposed1500V; otherwise it’s an annual inspection.For more details, please refer to SP D 79041 Section 10. |

|  |
| --- |
| **Insulation Resistance (IR) Test** |
| The IR test is conducted on the tool or equipment, section by section or as a complete assembly, in either a Dry or Wet condition.For more details and guidance refer to D2013/80872 section titled “IR Test Procedure”. |

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Date | Enter if Inspection or Wet/Dry IR test was conducted | Record IR value (MΩ) (Pass > 50 MΩFail < 50 MΩ) | Comments(e.g. condition of insulating surface) | Result(Pass or Fail) | Tested by(Name & Signature) |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |