|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Work Location: |  |  | Pole Number: |  |

|  |  |
| --- | --- |
| Number circuits 1 to 6 from top down.Include street lighting as a separate circuit. | CIRCUIT |
| 1 | 2 | 3 | 4 | 5 | 6 |
| Voltage |  |  |  |  |  |  |
| Owner / operator |  |  |  |  |  |  |
| Feeder number (high voltage) |  |  |  |  |  |  |
| Conductors damaged or down |  |  |  |  |  |  |
| Alive, dead, or earthed |  |  |  |  |  |  |
| Safe Approach Distance (m) (Refer below for mandated distances) |  |  |  |  |  |  |
| Safe Approach Distances visualised and related to landmarks? [Y/N] |  |  |  |  |  |  |
| Is the work above this circuit? [Y/N] |  |  |  |  |  |  |
| Is the work on this circuit? [Y/N] |  |  |  |  |  |  |
| Will workers climb through or past this circuit to work on other circuits? [Y/N] |  |  |  |  |  |  |
| Are live low voltage conductors spaced far enough apart to safely climb through? [Y/N/NA] |  |  |  |  |  |  |
| Will conductive equipment or conductors have to be raised or lowered through this circuit? [Y/N] |  |  |  |  |  |  |
| Other electrical pole hazards? [Y/N] |  |  |  |  |  |  |
| Permit number (if circuit is dead) |  |  |  |  |  |  |
| Has permanent insulation on the conductors been inspected? [Y/N/NA] |  |  |  |  |  |  |
| Is temporary LV cable cover required to be installed on low voltage conductors? [R/Y/N/NA] |  |  |  |  |  |  |
| Has the condition of this and adjacent poles and ties been checked? [Y/N] |  |  |  |  |  |  |
| Is it necessary to place a pole marker above this circuit? [Y/N] |  |  |  |  |  |  |
| Have any exposed earths been pointed out to all persons who will work on the pole? [Y/N] |  |  |  |  |  |  |
| Is a pole top rescue kit open and ready for use at the base of the pole? [Y/N/NA] |  | Have workers put on the required PPE (including working gloves)? [Y/N] |  |
| Can the work be done safely without persons or tools infringing the SAD’s? [Y/N] |  |  |  |  |  |  |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Voltage | 240/415V | 2.2-11kV | 22kV | 33kV | 66kV | 132kV |
| Safe Approach Distance (SAD) for authorised persons | 0.5m | 0.7m | 1.0m | 1.0m | 1.0m | 1.5m |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Legend | R: Required | Y: Yes | N: No | N/A: Not Applicable |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Completed by: |

|  |
| --- |
|  |
| Print |

 |

|  |
| --- |
|  |
| Signature |

 |

|  |  |  |
| --- | --- | --- |
|  | : |  |
| Time |

 | hours on |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | / |  | / | 20 |
| Date |

 |
| Checked by:(if completed by trainee) |

|  |
| --- |
|  |
| Authorised Person (Mains) or Overhead Worker Print |

 |

|  |
| --- |
|  |
| Signature |

 |

|  |  |  |
| --- | --- | --- |
|  | : |  |
| Time |

 | hours on |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | / |  | / | 20 |
| Date |

 |
| Work party: |

|  |
| --- |
|  |
| Signature |

 |

|  |
| --- |
|  |
| Signature |

 |

|  |
| --- |
|  |
| Signature |

 |

|  |
| --- |
|  |
| Signature |

 |
| This form must be used prior to work on poles supporting live exposed conductors or equipment. Refer to PR D 78108 for detailed instruction on how to use and complete this form. |